## Sheet2
Sl. No. | Item Code | Item Name | Unit | Qty | Item Specifications | Bidders Compliance | GSTpercent included in quoted rate | HSN Code
1 | 572530601R | Current-Pressure transducer | Nos | 50 | Electro pneumatic convertor required for BFP/FCV/FD/PA/ Burner tilt/ HPH/ LPH/ HFO/ LDO/ Dearator/ SH/RH/HAD/CAD services Make :Fairchild/Yokogawa/L&N/ Emerson/Watson Smith I/P signal: 4-20mA O/P signal : 3-15 PSI (0.2 - 1 kg/cm2) Calibration facility: both forward and reverse calibration Calibration required: forward Calibration characteristic : linear Media : compressed air Air supply : Compressed Instrument air 2.1 kSc Max I/P Pressure : 0-8 kSc Temperature Range: (-) 20 TO 85 DEG C End Connection :1/4" NPT (F) for supply & O/P with gauge port Mounting: Mounting Brackets with bolts and nuts to be supplied for 50mm OD pipe mounting Gauge: 40mm dial 1/4" NPT(M) Zero Adjustment : to be provided Span Adjustment : to be provided Minimum Span: 5 PsiG Reverse polarity : Protected Field reversability: Provided Impedence: 197 Ohms Supply Pressure: 20-120 PsiG Effect of supply pressure variation: 0.08% of span per psig change in supply pressure Response Time: 0.2 Secs from Zero to Span Terminal based linearity : 0.45% of Span Repeatability : 0.25% of span Hysterisis : 0.25% of span Flow rate: 5 scfm at 25 psig input Exhaust Rate: 2 scfm Air Consumption 0.14 CU METERS / HR Protection : IP67 Wiring Termination: DIN Plug Connector with Cable Gland IP-65 enclosure.